## Open Items
Item # | Description | Status | Target/Actual Completion Date
1 | Resolve Remaining MPSCS Punchlist items | See MPSCS Punchlist Tab | 2018-01-15
2 | MW Antenna System Decommissioning | In progress: Scheduled - Saugatuck-12/12, Lee-12/18, Dispatch-12/22, Wayland-12/20, Monterey-12/26, Valley-12/28…J. Harris to followup with Trent | 2017-12-31
3 | MPSCS Site 5502 ASR Site Conversion to Simulcast | Completed | 2017-12-06
4 | Wayland Antenna Move, including move of the Mutual Aid radio to the new combiner | Awaiting FCC license | 2018-01-31
5 | MCC7100 Implementation and Training | In progress, firewall issue to be resolved…should be simple fix - Tony Kurz and Tom Bryant to resolve | 2017-12-31
6 | Harris 800 MHz Decommissioning | In progress… Tele-Rad has no available crew until after FD installations, then will start decommissiong (1/15/2018 estimate) | 2018-01-31
7 | KVL Training | Per Theron Shinew, MPSCS will perform this training…R. Winters followup | 2018-01-31
8 | Final Documentation | Tabor to put all on a thumbdrive…Catherine Henning also needs, she will ping John Tabor | 2017-12-31
9 | Application of the GPS Location Licenses on the MPSCS UNS | Conference calls continue…New World not participating…options being explored…Allegan possibly consider system signoff provided Motorola continues to pursue | TBD
10 | Ensure that all items on RFP delivery list are satisfied | See Allegan RFP Items tab | 2017-12-31
11 | Signing any other required agreement documents | Jeremy states only outstanding agreements are MPSCS integration, Part 2 and co-location agreement…these are contignent upon getting equipment inventory from Motorola | 2017-12-31
12 | Reconciling any old Allegan County equipment that should go to Motorola | Jeremy to notify Motorola of any other equipment to be disposed of | 2017-12-31
13 | Complete installation of radios in fire vehicles | Tele-Rad is just over 50% complete…pace has been slowed to ensure quality of installations is not compromised | 2018-01-15

## MPSCS Punchlist
Source | Item # | Site # | Site Name | Deficiency | Notes | Responsibility | Target/Actual Completion Date | Updates
R56 | 3r | 5603 | Otsego | Bonding surfaces for lugs and clamps do not have a conductive anti-oxidant applied. There appears no anti-oxidant applied to the GPS antenna grounding kits at the EGB. |  | Mission 1 | 2017-12-08 | Complete
R56 | 3c | 5607 | Saugatuck | The tower ground bus bar (TGB) does meet the proper installation requirements. While checking the transmission line outer shield grounding kit connections on the TGB it was determined the TGB is not properly secured to the tower. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3c | 5607 | Saugatuck | The tower ground bus bar (TGB) does meet the proper installation requirements. The earth grounding electrode conductor is loose and needs to be properly secured. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3q | 5607 | Saugatuck | The transmission line outer shield grounding kits are not using approved securing methods on the TGB and the EGB. Multiple jumpers on the EGB and the TGB are secured to the bars using the same bolts. The same bolt or bolts may attach no more than one clamp, fitting or lug. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3q | 5607 | Saugatuck | The washers used on the transmission line outer shield grounding kits are overlapping the adjacent washer/connection. This does not allow for a solid connection to the TGB or proper torque on the connections. Correct size hardware shall be used. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3r | 5607 | Saugatuck | Bonding surfaces for lugs and clamps do not have a conductive anti-oxidant applied. There appears no conductive anti-oxidant has been applied to the Tower Ground Bus bar (TGB) where the transmission line outer shield is connected. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3t | 5607 | Saugatuck | Several transmission line grounding conductors on the EGB exceed the minimum bending requirements. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3t | 5607 | Saugatuck | Several transmission line grounding conductors on the TGB(s) exceed the minimum bending requirements. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3q | 5608 | Laketown | Approved methods have not been used for conductor connection and termination. A new TGB was installed and the old lines (many of the lines will be removed) were connected to the new bar. The VHF TX line’s grounding jumper is loose and needs to be properly secured. |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
R56 | 3r | 5608 | Laketown | Bonding surfaces for lugs and clamps do not have a conductive anti-oxidant applied. The connections to the generator do not have the paint removed and a conductive anti-oxidant applied. |  | Mission 1 | 2017-12-08 | Complete
R56 | 3t | 5609 | Monterey | Not all grounding conductors have been routed towards the EGB, TGB or the grounding electrode system and the minimum bending radius has not been observed. | Consideration may be given to move the TGB closer to the jumper attachment to the RF lines. | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Holmer | 6 | All | All | The cable trays have electrical outlets and conduit fastened directly to them with no isolators electrical installed. (All legacy Allegan County sites.) This creates multiple ground points for the cable tray. I was informed that these outlets would be removed during the decommission of the legacy radio system. |  | Mission 1 | 2018-01-31 | To be done at Harris 800 MHz decommission
Winters | 12 | 5504 | South Haven | Blue tape on transmission line needs to match the correct combiner 1 is going to 2 and 2 to 1 | Will and Rich to replace labels | MPSCS | N/A | Pre-existing
Winters | 13 | 5604 | Plainwell | Channel 5 failed the insertion loss check and channel 9 was right on the threshold for an 8-port combiner (column M on excel spreadsheet) | New combiner received, need to schedule installation | Tony | 2017-12-14 | Scheduled for completion on 12/14/17
Winters | 14 | 5604 | Plainwell | Blue tape on transmission line needs to match the correct combiner 1 is going to 2 and 2 to 1 | Will and Rich to replace labels | MPSCS | N/A | Pre-existing
Anway | 1 | All | All | All grounds need re-taping |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Anway | 2 | All | All | All angel adapters with ground wires to the need to be straitened |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Anway | 3 | All | All | All grounds to angel adapters need to be only one ground wire per adapter |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Anway | 4 | All | All | All stiff arms need to be re-tightened all locking nuts locked and all hardware tight this includes all fine adjust hardware and attach points to dish and tower |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Anway | 5 | All | All | Color coding tape fixed |  | Mission 1 | 2017-12-31 | To be done at MW antenna system decommission
Anway | 6 | All | All | Install MPSCS signage on compound gate | Signage has been received | Tabor / Mission 1 | 2017-12-15 | Trent to install on 12/15/17
Testing | 24 | 5609 | Monterey | Can't connect Light Alarms (Controller is in other bldg) |  | Allegan |  | JDH has looked at it and will provide a quote to Jeremy
Testing | 26 | 4 sites | All | Strap coolant level and coolant temperature alarms | Wolverine met with Steve Poole to resolve these | Mission 1 / Wolverine | 2017-11-29 | Complete
Testing | 27 | All | All | Can't test HVAC shutting off with smoke alarm because it's tied to the Halon | Allegan Halon contractor made modifications | Motorola / Allegan / MPSCS | 2017-12-06 | Complete
Alarms | 1 | 5603 | Otsego | Top Strobe | Controller burned up, parts ordered? Steve Poole is aware of this issue. | Allegan | 2017-12-08 | Resolved per Jeremy
Winters | New | 5602 | Wayland | Remove cable connecting VHF between buildings at Wayland | Jeremy to test to confirm if sirens can be activated without the Wayland site | Will Salefsle | 2017-12-31 | Test will be done on December 22. Rich Winters to designate proper cable to remove, and Jeremy will remove it on 12/22
Winters | New | 5602 | Wayland | Mutual Aid radio needs to be moved to the new combiner | To be done with antenna swap out | MPSCS/Motorola | 2018-01-31 | tied to FCC license approval
Winters | New | 5609 | Monterey | Still have low fuel alarm and smoke is beeping | Will to investigate
Anway | New | All | All | My request is to have 3 alarm points for fire suppression system. 1) smoke alarm 2) FCI trouble 3) halon release. The halon release alarm point will be a new alarm point that will need to be define what that alarm point will be. | Will to discuss how to accomplish this with Rich Winters | MPSCS/Motorola

## Allegan RFP Items
Item # | Description | Status | Target/Actual Completion Date
1 | Clean up all construction and installation trash | tied to 800 MHz. decommission task | 2018-01-31
2 | Ensure all NICE recording needs addressed | seems to be complete…Jeremy to check with Whitney and Megan | 2017-12-31
3 | Ensure final documentation includes all System Acceptance Test Data (RF power, antenna sweep info, etc.) | Tabor to put all on a thumbdrive…Catherine Henning also needs, she will ping John Tabor | 2017-12-31
4 | Disposal of all decommissioned equipment, antennas, coax, etc. | tied to 800 MHz. decommission task | 2018-01-31
5 | Provide all keys, passwords, etc. needed for routine operation and maintenance | per John Tabor, will be included with documentation thumbdrive | 2018-01-31
6 | Provide complete equipment inventory database of all sold and installed | Tabor to put all on a thumbdrive…Catherine Henning also needs, she will ping John Tabor | 2017-12-31
7
8
9
10
11
12